## Municipal Projects
Project Name | Ridgebury Elementary School (Ridgefield Public Schools) | Ridgefield High School (Ridgefield Public Schools) | Scotland Elementary School | Veterans Park School (Ridgefield Public Schools) | Fitch High School (Groton Public Schools) | Branford High School (Branford Public Schools) | Branford Police Department | Kent Sewer Commission
Address | 112 Bennetts Farm Road, Ridgefield, CT | 700 N Salem Rd Ridgefield, CT | 111 Barlow Mountain Rd, Ridgefield, CT 06877 | 8 Governor Street Ridgefield, CT | 101 Groton Long Point Road, Groton, CT | 185 E Main Street Branford, CT | 33 Laurel Street, Branford, CT | 125 Schaghticoke Rd, Kent, CT 06757
System Size KW DC | 243 | 1046.33 | 576.22 | 430.59 | 1180 | 820 | 55 | 250
System Size KW AC | 191 | 871.94 | 453.72 | 339 | 850 | 700 | 43 | 196.85
Year 1 Production Estimate Based on Prelim design (kWh) | 291597 | 1255599.6 | 691468 | 516711.6 | 1404864 | 1008188 | 66000 | 300000 (system design not to exceed 222,000 kWhs)
Proposed System Type | Roof + Carport | Roof + Carport | Rooftop+Carport | Rooftop | Carport | Rooftop | Rooftop installation on pre-exisiting carport structure | Ground Mount Installation
Utility | Eversource | Eversource | Eversource | Eversource | Eversource | Eversource | Eversource | Eversource
PID | 2115 | 975 | 2495 | 5677 | 260809251571 E | 389 | 374 | 239
Eligible for NRES Green School Carveout? | Yes | Yes | Yes | Yes | Yes | Yes | No | No
Tariff Agreement Secured? | No | No | No | No | No | No | No | No
Tariff Structure | Open to either BASA or Netting | Open to either BASA or Netting | Open to either BASA or Netting | Open to either BASA or Netting | Open to either BASA or Netting | Netting and BASA | Open to either BASA or Netting | Open to either BASA or Netting
New Construction | No | No | No | No | No | No | Carport structure is new construction, designed to be solar ready. Advised that conduit for solar should be included | No
Snow Guards Required | Yes (carports) | Yes (carports) | Yes (carports) | N/A | Yes | N/A | Snow guards being installed on carport structure. Contractor to evaluate if removal is required for solar install. If so, new snow guards should be included in solar scope. | N/A
Carport Height | 14'. If carports are included in the design, property owner has asked bidders to consider including rubber gaskets in between the modules to prevent water runoff and the creation of ice (not required) | Have existing carport installation in parking lot to the West. Open to add on system in Eastern and Northern Lot. 14' clearance required for carport. Note that the Eastern lot is emloyee parking and there is a water main underground that will be undergoing construction in the summer of 2026. If carports are included in the design, property owner has asked bidders to consider including rubber gaskets in between the modules to prevent water runoff and the creation of ice (not required) | 14' If carports are included in the design, property owner has asked bidders to consider including rubber gaskets in between the modules to prevent water runoff and the creation of ice (not required) | N/A | 12' | N/A | N/A | N/A
Acceptable working hours/ day | Construction is limited to after hours, evenings or weekends during the school year. Open access for construction during the summer (Summer is 6/25-9/1). | Construction is limited to after hours, evenings or weekends during the school year. Open access for construction during the summer (Summer is 6/25-9/1). | Construction is limited to after hours, evenings or weekends during the school year. Open access for construction during the summer (Summer is 6/25-9/1). | Construction is limited to after hours, evenings or weekends during the school year. Open access for construction during the summer (Summer is 6/25-9/1). | Monday - Friday; construction will need to be phased if started during school year. No restriction on start or end time but 8:00 AM arrival is recommended due to bus arrival times. End of school traffic will be between 2-3 PM. | During School Breaks, most weekends, outside of school hours 6 AM to 5 PM. Branfords preference is for construction to take place during the summer break to avoid disruption to the school community. If construction is to occur during the school year, additional coordination around athletics will be required. Typical school calendar can be found here: https://resources.finalsite.net/images/v1759496569/branfordk12ctus/xuqlfcgjqt2cfcd3crnw/Corrected2526Calendar.pdf | No restrictions on working hours. Can work week days and weekends if needed. | 7 AM 4:30 Monday through Friday
Calendar Restrictions | Construction is limited to after hours, evenings or weekends during the school year. Open access for construction during the summer (Summer is 6/25-9/1). | Construction is limited to after hours, evenings or weekends during the school year. Open access for construction during the summer (Summer is 6/25-9/1). | Construction is limited to after hours, evenings or weekends during the school year. Open access for construction during the summer (Summer is 6/25-9/1). | Construction is limited to after hours, evenings or weekends during the school year. Open access for construction during the summer (Summer is 6/25-9/1). | None | Evenings, Weekends, Holidays are acceptable for work. | None | No Holidays or weekends
Security Protocols | All Personnel must be cleared by onsite security; List of names should be presented to the school; ID for onsite personnel required | All Personnel must be cleared by onsite security; List of names should be presented to the school; ID for onsite personnel required | All Personnel must be cleared by onsite security; List of names should be presented to the school; ID for onsite personnel required | All Personnel must be cleared by onsite security; List of names should be presented to the school; ID for onsite personnel required | List of individuals onsite to be provided to the school; background checks required at contractors expense | Contractors cannot enter the building or have any direct student contact. If the contractor does, they need to have fully completed background checks at their expense. They also need to be insured and name the Town of Branfrod/BOE as additional insured | Valid government ID required for all contractors/visitors to the facility. Will need to pre-plan work days to prepare for arrival of crews on sight, provide access to necessary parts of the building and relocation of fleet vehicles if necessary. | Chain across entryway with Padlock and padlock on gate for main interest. Opened at 7 AM for access to the site.
Electrical/Structural Drawings available? | Staff is looking for digital drawings to share. If available Green Bank will circulate post RFP release. Potential that paper drawings exist; inquire while onsite for site walk. | Staff is looking for digital drawings to share. If available Green Bank will circulate post RFP release. Potential that paper drawings exist; inquire while onsite for site walk. Switchgear for Meter # 081004291 appears to be 480/277 V 3000 A service. Switchgear for meter #081216301 appears to be 480/277 V 2000 A service. 3 Line wiring diagram for most recent carport project included in Exhibit A. Note that the site is having work completed on the water main. They are looking for an underground utility map for review. | Staff is looking for digital drawings to share. If available Green Bank will circulate post RFP release. Potential that paper drawings exist; inquire while onsite for site walk. 2500 Amp 208 Volt Service at Barlow Mountain Elementary (if needed for the carport install.) | Staff is looking for digital drawings to share. If available Green Bank will circulate post RFP release. Potential that paper drawings exist; inquire while onsite for site walk. | Some paper drawings available; ask during site visit. | Physical Blueprints available for review onsite. Drawings also uploaded in Exhibit A. Building was constructed in 3 phases: Original construction in 1958, additions in 1978 and 1998. BOM/Scope of work for switchgear upgrades included in Exhibit A. | See Drawings included Exhibit A including: site layout plan, carport framing plans and sections, general notes and typical details, carport plans and details, carport section and details, site utility plan, carport electrical plans, site lighting plan | Some electrical drawings available and included in Exhibit A. Please ask to view onsite. Drawings showing underground utilities/piping around the treatment plant also uploaded. We have been advised that the information becomes less reliable the closer you get to the buildings. Oakwood Environmental Associates has recommended that test pits be performed at the anticipated location of the foundation. Respondents should budget for survey work to verify prior to construction.
Roof Warranty Info | Site roof was recently replaced (entire facility; existing solar was re-installed). 32 Year warranty. Effective date is 9.1.2025. Silktown Roofing was the Contractor. Installed StressPly Legacy DR Mineral Roofing. Warranty issued through Garland Company, Inc. | 32 Year warranty. Effective date is 9.1.2025. Silktown Roofing was the Contractor. Installed StressPly Legacy Roofing. Warranty issued through Garland Company, Inc. New section of the roof being re-roofed prior to 10.1.2026. See exhibit A - 'Area of the roof being replaced' for available area. | 32 Year warranty. Effective date is 8.22.2025. Barrett Roofing Co was the Contractor. Installed StressPly Legacy FR Roofing. Warranty issued through Garland Company, Inc. | Roof replacement funding and scope approved with installation to be completed by 10.2026. Design is still being finalized so there is no spec sheet included in this RFP for the anticipated re-roof | N/A | Roof is being replaced and is being phased in over summer 2026 and summer 2027. Interim funding request was approved by the BOE on 10/30/2025. EPC to follow up on roof warranty documentation prior to install. Roof Key included in Exhibit A which includes SF by section of the building, original construction date. | No warranty documentation for the metal roofing has been submitted to date. The approved product submittal is included in Exhibit A. The forthcoming warranty documentation will be reviewed for alignment with the requirements enumerated in Section 076100-1.6 of the specifications provided. Product is required to have a 20 year arranty against rupture, cracks, or perforation due to corrosion. 20 year warranty for finish against peeling, blistering and chalking. 10 year warranty for wather tightness. Awarded EPC to follow up on warranty documentation prior to install. | N/A
FM Global Insured? | No | No | No | No | Unknown, School is confirming | No | No | No - CIRMA
Important General Notes | 1 utility meter. Existing BTM solar install (rooftop). Billing Account #51906043054; Meter # 034905052. Analyzed Billing Period 11.15.2024-10.16.2025 = 248,280 kWhs. Rate 30. Utility Bills + Totalized Load Included in Exhibit A. Summary across all utility accounts also included should additional load be required to justify a proposed system size. Due to the requirement in the school carveout that school projects only qualify for the carport adder for 100% carport projects, respondents should provide pricing for carport only design and a hybrid design (rooftop + carport). Required shutdown to take place after school hours. | 2 Utility Meters: 1) 081004291 (Account #51557223054); Rate 58. Existing behing the meter solar (ZREC install) + Buy All Sell All NRES Tariff project 2) 081216301 (Account #51768453060); Rate 56. Existing ZREC BTM Solar install (rooftop). Switchgear for Meter # 081004291 appears to be 480/277 V 3000 A service. Switchgear for meter #081216301 appears to be 480/277 V 2000 A service. Photos included in Exhibit A. Respondents should also field verify during the site visit. Modeling may be for solar as a standalone option, battery storage as an individually priced option, or solar + battery storage as a paired project. Interval data uploaded for review and consideration. Re-roof for select area anticipated to be complete by 10.1.2026. See exhibit A - 'Area of the roof being replaced' for available area. Utility Bills + Totalized Load Included in Exhibit A. Summary across all utility accounts also included should additional load be required to justify a proposed system size. Due to the requirement in the school carveout that school projects only qualify for the carport adder for 100% carport projects, respondents should provide pricing for carport only design and a hybrid design (rooftop + carport). Required shutdown to take place after school hours. Most recent carport installation received PTO 10.1.2025 | Existing BTM solar (130 kW DC PPA). System was removed and the entire roof was replaced. Solar shown on aerials is being re-installed post re-roof. Looking to add second rooftop solar project in unused space + carport canopy. Utility Bills Included in Exhibit A. Rate 30A. Billing Account #51179043070; Meter #034278782. Summary across all utility accounts also included should additional load be required to justify a proposed system size. If Carport +Solar requires a service upgrade, Carport can be tied to Barlow Mountain Elementary School next door. Note that a ZREC expired at Barlow Mountain Elementary in late 2025; requiring a 1 year delay before a new submission in the NRES program. Due to the requirement in the school carveout that school projects only qualify for the carport adder for 100% carport projects, respondents should provide pricing for carport only design and a hybrid design (rooftop + carport). Required shutdown to take place after school hours. | 1 utility meter. Rate 40. Roof to be replaced by 10/2026. Utility Bills Included in Exhibit A. Summary across all utility accounts also included should additional load be required to justify a proposed system size. Required shutdown to take place after school hours. | 2 Utility meters/accounts onsite: ending in 4099 and 2010. Billing Account 5198 073 4099; Meter # 081032071 is rate 56. Total kWh load over 12 months (June 2023-June 2024) = 644,400 kWhs. 2000 Amp 480Y/277V service. Billing Account 5180 469 2010; Meter # 081032051 is rate 37. Total kWh load over 12 months (June 2023-June 2024) = 997,248 kWhs. 2000 Amp 480Y/277V service. Planned conduit run to be reviewed and approved with the site. Re-roof likely for facility in near term. Concern running conduit over roof to point of interconnection identified on the site report provided. | Small rooftop solar installed onsite - will be removed as part of the anticipated re-roof. The school does not plan to re-install. District has 4 x 65 kW existing COGEN that operate at 200 kW and is evaluating installation of a new COGEN system for the site (or alternate technologies). (NOTE: this work would likely not commence until the spring or summer of 2027. ) Design should be rooftop only. Interval data saved in Exhibit A. Modeling may be for solar as a standalone option, battery storage as an individually priced option, or solar + battery storage as a paired project. ELECTRIC ACCOUNT DETAILS-Peak Annual Usage: 87,240 kWh (10/2023 - 9/2024)-Third Party Supplier: BP Energy Retail Company-Third Party Supply Rate: $0.10679 / kWh -Utility-Owned Transformer -ID: 397 -kVA Nameplate: Unknown. Upgrades to the switchgear planned for summer of 2026. BOM/Scope of work for the switchgear upgrade included in Exhibit A. The scope of work is to replace the aging electrical infrastructure so that the school can adequately accommodate the daily operational needs. | Carport Structure will be installed by the Town of Branford at their own cost. Structure will be solar ready and will include: -Standing Seam metal Roof with snow guards -Under canopy lighting (refer to carport lighting plan) -Lightning protection -Metal gutter and downspout -Underground electrical conduit - Designed for 3 PSF of solar - Construction completion estimated April 2026 Construction Manager (Contractor): Downes Construction Company, LLC, 200 Stanley Street, New Britain, CT 06051 (860-229-3755) Electrical Engineer: Innovative Engineering Services, LLC, 33 N Plains Industrial Road, Wallingford, CT 06492 (203-467-4370) Structural Engineer: Szewczak, Kilty & Fluhr Structural Engineers, P.C., 60 Avon Meador Ln Unit D, Avon, CT 06001 (860-677-4570). Utility Account Info: Account # 5105 170 3031; Meter # 896361352; 12 Months of Load Data (April 2023-April 2024) = 286,700 kWhs; Rate 30 | The sewer plant is on property owned by Kent School. Note that there are 2 desktop review reports uploaded: 1) dated 10.2.2020 which is a smaller array designed based on the load for the facility at that time and 2) a second report dated 10.7.2025 sized based on the available usable ground space. Respondents should size the project to not exceed 222,000 kWhs for the total production. A copy of the 3 utility bills paid by the sewer commission are included in Exhibit A: 1) Account # 5154 572 3082; Meter #034275332 Rate 116; 2) Account # 5163 729 6070; Meter # 892593972 Rate 30 3) Account # 5104 172 3065; Meter # 892908572 Rate 30. Utility Bill for the Town Hall is also included. Totalized load across all 4 utility bills is ~222,000 kWhs. Respondents should be cognizant of underground utilities when designing this project.
Single Phase vs Three Phase? | Three Phase | Three Phase | Three Phase | Three Phase | Three Phase | Three Phase | Three Phase | Three Phase
Hosting Capacity (as of 1.16.2026) | 300 kW on Circuit 22N1 | 1 MW on Circuit 22N5 | 700 kW on Circuit 22N5 | 300 kW on Circuit 22N3 | 200 kW on Circuit 11B1. Green Bank intends to submit for interconnection as close to the original proposed system size as possibe. Interconnection Upgrades should be excluded from EPC pricing provided. We kindly request respondents provide a design and pricing for a layout that matches or closely aligns with the site report provided. We also ask for an option B which would be pricing for a 200 kW AC system size to match the available hosting capacity, as currently indicated on the available hosting capacity maps. | 2.4 MW on Circuit 11J43 | 1.2 MW on Circuit 11J43 | 200 kW on Circuit 11M3
Generator? | Full Load Standby Generator | Partial Load Generator | No Generator | No Generator | Partial load generator onsite | No generator onsite currently, but is being discussed as a possible addition. | Generator being installed as part of onsite construction project (not part of the solar scope). Generator is a full load generator. | Diesel generator - full load for the plant.

## Affordable Multifamily Projects
Project Name | Mauro Meadows | 55 Nye Road (Glastonbury Housing Authority) | Parish Court | Shad Run Terrace (Windsor Housing Authority) | John Fitch Court (Windsor Housing Authority) | Southwest Terrace Apartments (Windsor Locks Housing Authority) | Colonial Village (Norwalk Housing Authority) | Sheldon Oak - Vine Street | Rochambeau Apartments | Room Unity | Oak Tree Village Phase I & II
Address | 3-17 Trinity Hill Dr, Durham, CT 06422 | 55 Nye Road Glastonbury, CT | 185 Warde Terrace, Fairfield, CT 06825 | 40 Henry Street Windsor, CT | 156 Bloomfield Ave, Windsor, CT 06095 | 124 Southwest Ave, Windsor Locks, CT 06096 | 0 Suncrest Rd & 164 W. Cedar St, Norwalk, CT 06854 | 39-49 Vine Street; 44,48.52 Vine Street | 68 Silver Lane, East Hartford, CT 06118 | 666 Main Street, Middletown, CT 06457 | 97 Preston Road Griswold, CT
System Size KW DC | 127.8 | 200 | 302.72 | 202.75 | 340.2 | 337.36 | 875.16 | 154.87 | 128.6 | 61 | 273.06
System Size KW AC | 100 | 157.48 | 220 | 140 | 280 | 300 | 630 | 122 | 103.8 | 49.59 | 222
Year 1 Production Estimate Based on Prelim design (kWh) | 117639 | 240000 | 318510.4 | 208554 | 357839.8 | 351775.3 | 925987.1 | 185842.67 | Site Report designed for 143,850 kWhs. Max Buildable System Size is 168,276 kWhs | 73200 | 327674.1
Proposed System Type | Rooftop | Rooftop | Rooftop | Rooftop | Rooftop + Carport | Carport | Rooftop | Rooftop | Rooftop | Rooftop | Rooftop
Utility | Eversource | Eversource | UI | Eversource | Eversource | Eversource | Eversource | Eversource | Eversource | Eversource | Eversource
PID | D0083700 | 12287 | 2916 | 838 | 4748 | 406400 | 22015 | 198-214-44;198-208-130 | 12885 | 390 | 3266 + adjacent parcel (phase II)
Tariff Structure | RRES MFAH Program - BASA | RRES MFAH Program - BASA | RRES MFAH Program - BASA | RRES MFAH Program - BASA | RRES MFAH Program - BASA | RRES MFAH Program - BASA | RRES MFAH Program - BASA | RRES MFAH Program - BASA | RRES MFAH Program - BASA | RRES MFAH Program - BASA | RRES MFAH Program - BASA
Individually vs Master Metered | Individually metered, tenant paid utilities. | Individually metered, tenant paid utilities. | Master Metered facility. | Individually metered, tenant paid utilities. | Individually metered, tenant paid utilities. | Individually metered, tenant paid utilities. | Individually metered, tenant paid utilities. | Individually metered, tenant paid utilities. | Individually metered, tenant paid utilities. | Individually metered, tenant paid utilities. | Individually metered, tenant paid utilities.
On the Tier 1 List | Yes | No - LIHTC Project. Will be added to the list upon award. | Yes | Yes | Yes | Yes | Yes | 39-49 Vine Street is on the Tier 1 List (Vine Rehoboth); 44,48,52 Vine Street will need be qualified for participation. Confirmation has been received that site will meet affordability requirements to participate. | No, Tier 2 Project. Prequalified to participate in the RRES MFAH Program | Not on the Tier 1 or Tier 2 list; rent rolls reviewed. Will qualify as a NOAH site. | Oak Tree Village Phase I is on the Tier 1 List. Phase II is a LIHTC Project. Will be added to the list upon award.
Verified Load with the Utility | 218,696 kWhs | New Construction - can size up to 9 kW AC per unit. | 711,063 kWhs (12 month verified load) Max allowable with 5% overage = 746,616 kWhs | 433,677 kWhs | 532,432 kWhs | 276,759 kWhs (Note system size outlined on site report will need to be reduced to be at or below this production figure.) | 2,507,673 kWhs | Not yet verified with the EDC; load verification pending. | 168,276 kWhs. | Not yet verified with the EDC; load verification pending. | 9 kW AC per unit allowable for Phase II which is new construction. Load for Phase I has not yet been verified, max out available roof space for both.
New Construction | N/A | Yes | N/A | N/A | N/A | N/A | Yes - construction complete | Going through LIHTC Renovation; submittal is under the preservation category. | No | No | Phase I was complete ~ 2021. Phase II will be new construction
Snow Guards Required | N/A | N/A | N/A | N/A | Yes for carports | Yes for carports | Yes (if carports included in design) | N/A | No | N/A | N/A
Squirrel Guards Required | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | No
Carport Height | N/A | N/A | N/A | N/A | 12' | 14' | Clearance requirements must be confirmed with the City Ordinances and Setbacks.* See note below on carports* (If carports included in design - site report is for rooftop only installation) | N/A | N/A | N/A | N/A (carports shown on phase 1 desktop review. Please disregard and proceed with rooftop only modeling.)
Acceptable working hours/ day | 8-4 Monday through Friday; weekend work allowed with prior permission | 7-4:30 Monday through Friday | Monday - Sunday 8 AM to 6 PM allowed (must be during working hours when Maintenance Staff is on site.) | Monday - Friday 8 AM to 6 PM. Saturdays are acceptable if needed but will need to be flagged for the Housing Authority. Respondents can work until 7 PM during spring and summer timeframe if needed. | Monday - Friday 8 AM to 6 PM. Saturdays are acceptable if needed but will need to be flagged for the Housing Authority. Respondents can work until 7 PM during spring and summer timeframe if needed. | Monday - Friday 8 AM to 5 PM. | 8 AM to 4 PM | 8 AM to 5 PM Monday through Friday. Weekend Hours: 9 AM to 5 PM. Hours for noisy activities shall be limited to the hours of 10 AM to 5 PM. Advance notice should be given (2 days) for high levels of noise or other disruption. | 8 AM to 4 PM | 9 AM to 10 PM | 9 AM to 5 PM Monday -Friday
Calendar Restrictions | Holidays ok with permission | No weekends or Holidays unless approved by the site owner | Closed on Federal Holidays only | None, acceptable to work on Holidays so long as this is pre-arranged so notice can be given to residents | None, acceptable to work on Holidays so long as this is pre-arranged so notice can be given to residents | Cannot work on weekends or Holidays | Construction restricted on Federal Holidays | No restrictions | Construction restricted on Holidays | None, weekends and holiday construction allowed. | Construction on Holidays is acceptable with notice to property owner
Security Protocols | If you need access to certain areas maintenance staff will need to be there | N/A | None | None. | None. | None. | Staff will accompany contractors to the site. | As this is a LIHTC project, we have verified with the investor that construction of the solar portion of the project can start prior to the LIHTC construction project being completed. Meaning that once the roof is replaced, onsite work can begin as other non-roof related projects begin. If the selected EPC contractor decides to proceed in this manner, there will need to be coordination between the selected contractor and the GC, including security protocols, job safety, insurance, etc. If construction begins while the broader LIHTC construction project is underway, the property owner will have on-site security for the duration of the LIHTC construction work. Alternatively, the selected EPC contractor may elect to wait until the LIHTC project is complete to avoid overlap with other contractors working onsite. If this is pursued, respondents should be aware of the overall anticipated project timeline. As it currently stands: CHFA board approval anticipated March/April 2026. Closing to take place within 60 days, likely June/July 2026. LIHTC Construction will commence immediately with roughly a 14-month timeline. Full completion anticipated Q3/Q4 2027. 39-49 Vine Street include 15 total Units across 2 buildings. 44, 48, and 52 Vine Street have 42 total Units across 3 Buildings. All buildings are individually metered with tenant paid electric. | None noted | None | Passcode required for interior access. Prior coordination with staff required for access to electrical rooms.
Electrical/Structural Drawings available? | Blueprints available for the site (paper copies). Please ask to review during the site visit | See issued for construction Drawings included in Exhibit A | Unsure if drawings are available. Please ask to view during the site visit and if located prior drawings will be made available. | Unsure if drawings are available. Please ask to view during the site visit and if located prior drawings will be made available. | Unsure if drawings are available. Please ask to view during the site visit and if located prior drawings will be made available. | Unsure if drawings are available. Please ask to view during the site visit and if located prior drawings will be made available. | See Drawings included in Exhibit A | 90% drawing set included in Exhibit A | See Drawings included in Exhibit A | None available | As Builts for Phase I provided; IFC set for Phase II Provided.
Roof Warranty Info | Roofing is asphalt shingle. Site is working on locating roof warranty documentation. It is anticipated that this is a 50 year asphalt shingle with installation taking place either in 2010, or in 2018 (which would have been through a small cities grant.) | New Construction - awardee to collect roof warranty info for overburden waiver process prior to construction. 30 Year Architectural Asphalt Shingle Roof planned. | Roof was installed in 2011 and has a 30 year warranty. GAF Timberline architectural shingles. Property owner is deciding between roof replacement and proceeding with the project as is. The board has approved the roof replacement if they decide on that course of action. Replacement prior to install would be at property owners expense. Summer/Fall 2026 install. | Grant secured for roof replacement prior to solar installation. Please see Permit Set included in Exhibit A. The overall site plan is on A1.0, each building indicates a roof type that can be found on the following pages. Roof Plans for can be found starting on: A1.1 – Community Building A1.2 – Building Type B A1.3 – Building Type C A1.4 – Building Type D A1.5 – Building Type E A1.6 – Building Type F Work anticipated to be completed in Spring 2026 | Roofs were replaced in 2024 and are under warranty. Expiration 10.22.2044. EPDM and PVC roofing. Roof warranty documentation saved in Exhibit A. | N/A | Yes, phased install from 2021-2023. Install date by building and associated warranty documentation/ roof disclosure form available for review. | Roofs being fully replaced as part of the renovation project. .060 TPO – 20-25 year warranty anticipated. Awarded EPC to follow up on roof warranty documentation for overburden waiver purposes prior to installation. | Roof warranty and disclosure form included in Exhibit A | Roof Replaced in 2022 by previous owner. No roof warranty documentation was located prior to the publishing of this RFP. Signed roof disclosure form included in Exhibit A. | Phase 1 construction completed in 2021, asphalt shingle roofing. Phase 2 Construction to be complete in mid -2027. Phase 2 is new construction. Brand new roof to be installed. Awarded EPC to follow up on roof warranty documentation prior to installation for overburden waiver purposes.
Important General Notes | Individually metered, tenant paid utilities. Generator onsite for community building only. Gridtwin shows a potential utility upgrade required. Respondents should exclude upgrade cost from EPC pricing provided. | Timeline: Board Approval anticipated in March 2026. Closing on funding in May 2026. Construction start anticipated in April 2026 time frame. The first building is anticipated to be completed in January 2027. The last building will be finished October 2027. The site is Individually metered with tenant paid utilities. 20 total buildings. 64 total Units. Site Civil = Benesch; Structural Engineer = PES; MEP Engineer = Acorn. Roof Plans included in drawing set. 30 Year Architectural Asphalt Shingle Roof. Generator for community building only. Timing for onsite construction activities: CHFA has confirmed that the solar install is not required to be completed at the same time as the facility construction. Respondents should note that the site is tight and coordination will be required for laydown/staging. Modeling may be for solar as a standalone option, battery storage as an individually priced option, or solar + battery storage as a paired project. | Master Metered facility. No tree removal assumed in site report provided. If required, respondent should flag in their proposed design and include the cost in their scope of work. 50 kW AC cap per system (single phase site). 6 single story buildings. Generator onsite for main building. | Systems are capped at 50 kW-AC (single phase). Transformer configuration is assumed based on Tx location and building/meter layout, confirm with EDC. Site report proposes 4 Trees be removed. Cost to do so should be included in the EPCs pricing and scope of work. Contractors to provide porta potties - building closed to workers onsite. Site is open to carport canopies if a design expansion is economically viable. | One tree flagged for removal as part of the preliminary design provided. Cost for tree removal should be included in EPCs scope of work/pricing provided. Site is powered by 3-phase transformer and EDC will not limit maximum system size (beyond onsite load flagged above). Proposed site report provided has the rooftop and solar combined into one system, with one RRES incentive and one interconnection application. Respondents should model the most cost effective solution, which can include multiple interconnection applications if required. Solar will interconnect at new front-of-the-meter electrical service. Equipment/material to be purchased in bulk for entire site. Roofs were replaced in 2025 and are under warranty. Limited exterior wall space adjacent to electrical room, new PV equipment will be mounted on the ground adjacent to existing utility-owned transformer. Please refer to site report included in Exhibit A. Listed in National Register District & State Register District. Contractors to provide porta potties - building closed to workers onsite. Property owner has flagged that heat pumps are to be installed on the roof. Modeling may be for solar as a standalone option, battery storage as an individually priced option, or solar + battery storage as a paired project. | Existing Behind the meter solar to remain. Site is powered by 3-phase transformer and EDC will not limit maximum system size (beyond onsite load flagged above). Solar will interconnect at new front-of-the-meter electrical service. Equipment/material to be purchased in bulk for entire site. Five trees to be removed as part of the project scope. Cost should be included in EPC pricing provided/scope of work. Contractors to provide porta potties - building closed to workers onsite. 276,759 kWhs is the verified load for this site. Please note that the system size outlined on site report will need to be reduced to be at or below this production figure. Modeling may be for solar as a standalone option, battery storage as an individually priced option, or solar + battery storage as a paired project. | Site report provided is for a rooftop only project. Per the recent EDC limitation for single phase sites, systems are capped at 50 kW-AC / 75 kW-DC. If there is a cost effective option to do so, property owner is open to rooftop only or rooftop + carport canopy designs. Comments included on the project site report are specific to the layout included in Exhibit A. Respondents should review and inform their own design based on the criteria outlined in this RFP. Buildings in a PV system may not necessarily be powered by the transformer the PV system interconnects to. The layout provided assumes a new set of secondary conductors will be pulled from the transformer and routed to the new solar equipment. For each system the new solar equipment will be mounted on the exterior wall of one building. Depending on the exact design, either AC or DC conductors will be routed via underground conduit to combiners on the exterior of the building with the new PV equipment; No generators onsite. Individually metered, tenant paid utilities. 200 total Units. | See general timelines outlined above. Certificate of insurance naming the owner entity (Vine Rehoboth LLC) and property manager (Millennum Real Estate Services, LLC) should be provided. Coverage limits must meet Green Bank insurance requirements as outlined in our EPCA as well as the CHFA requirements included in Exhibit A. Should the solar installation work coincide with permanent mortgage conversion, contractor lien releases may be required. Heat Pumps are no longer anticipated for this project. Respondents should disregard on the drawings and maximize the solar layout. Respondents are not required to follow the solar footprint included in the 90% drawing set. | Existing solar on common area space. See drawings in Exhibit A. Generator for critical loads tied to Units 1-23. Site is individually metered with tenant paid utilities. 56 total meters onsite. 5 owners meters, 50 tenant meters, and 1 PV Production meter. | 18 Units. Tenant Paid Electric (will fall under the individually metered program rules). Site qualifies as naturally occurring affordable housing (NOAH) based on rent roll provided. Approval from PURA will be required for participation. Green Bank will handle this request. No onsite generator. Site has advised that they can make space in the parking lot area for staging. Lock Box for access to the site will be made available to contractors. Lock Box can be found on the Rappallo Ave Entrance. There is a roof hatch for access to the roof. Parking will be available in the lot off of Green Street. | Phase 1 - Existing Building 72 Units Site is individually metered with residents paying their own electric bill 2 Backup generators onsite. Natural gas, for common area space only. 2021 construction Solar installed on common area space of phase 1. For Phase 1: Structural Engineering by Structural Integrity; Mechanical by Allied Engineering; Civil by Alfred Benesch and Company; Interior design by TMD Designs. Phase 2 - New Construction 60 Units yes Residents pay their own electric bill (Owner pays for heating/cooling/hot water, tenant pays for cooking and lighting.) 2 backup generators. Emergency loads only. Construction to commence immediately upon LIHTC closing. 14 month construction timeline. Estimated completion July 2027. For Phase 2: Architect: Ed Wojcik, Architect, Ltd; Electrical Egineer: Wozney Barbar Engineering; Mechanical Engineer: Wilkinson Associates; Civil Engineer: Alfred Benesch and Company; Structural Engineer: GNCB Consulting Engineers.
Single Phase vs Three Phase | Single Phase | Three Phase | Single Phase | Single Phase; 3 Phase starts at Midian Ave | Three Phase | Three Phase | Single Phase | Three Phase | Single Phase | Three Phase | Three Phase
Hosting Capacity (as of 1.16.2026) | 50 kW AC on Circuit 30k14 | 600 kW on Circuit 22R6 | 670.20 kW on Circuit 2690 | 50 kW AC on Circuit 24J1 | 1.2 MW on Circuit 24J6 | 400 kW on Circuit 14K5 | 1 MW on Circuit 24A13 | 4.3 MW on Circuit 300U2 | 50 kW AC Circuit 32G13 | 1.4 MW on Circuit 7A76 | 200 kW on Circuit 12S1
Generator Onsite? | Generator for community building only. | Generator for community building only. | Generator onsite for main building. | No | No | No | No | Unknown | Partial for critical loads | No | 2 backup generators at both Phase I and Phase II
Battery Storage Modeling Requested? | No | Yes | No | No | Yes | Yes | No | No | No | No | No